COIL COATING SPECIFICATION

# Corrosion-protection coating of HVAC coils and heat exchangers

Template for tender and purchase documents. Replace every field in [brackets], delete clauses that do not apply, and keep the clause numbers. The template describes performance and evidence, not a coating brand.

# 1. Project data

| Item | Value |
| --- | --- |
| Project | [project name and location] |
| Equipment | [condenser coils / evaporator coils / outdoor units / chiller coils / dry coolers / other] |
| Coil type | [copper tube, aluminium fin / microchannel (all aluminium) / copper fin / other] |
| Quantity | [number of coils or units, models or coil dimensions] |
| Fin density | [fins per inch or fin pitch in mm] |
| Destination and site | [country, city; distance from the sea in km] |

# 2. Site conditions

2.1  Site atmospheric corrosivity category to ISO 9223: [C3 / C4 / C5 / CX].

2.2  Additional exposure: [none / industrial pollution / acid gases / H₂S / ammonia / chemical splash / indoor pool air].

2.3  Where the site category is not known, it shall be estimated from distance to the sea, humidity, nearby industry and shelter, and the basis stated.

# 3. Scope of coating

3.1  Coils shall be coated after fabrication. The coating shall cover fin faces, fin edges, fin collars, tubes, return bends, headers and brazed joints.

3.2  Pre-coated fin stock (for example blue or gold fin) does not by itself meet this clause.

3.3  Complete units that cannot be oven-cured shall be coated with an ambient-cure system after masking of controls, sensors, terminals, valves and refrigerant connections, or the coil shall be removed, coated and cured separately, then refitted and pressure-checked.

# 4. Coating system

4.1  Coating system: [chemistry or product] or equal. Equality is demonstrated by the evidence required in clauses 6 to 8.

4.2  The technical data sheet (TDS) and safety data sheet (SDS) shall be submitted for approval before production.

4.3  The coating shall be suitable for the coil metals listed in clause 1. Suitability for copper shall be stated in the TDS where the coil contains copper.

# 5. Application

5.1  Application method: [dip / spray / flood / full-unit]. Dip application is preferred for loose coils that fit the tank.

5.2  Surface preparation: degreasing, rinsing and drying so that the surface is free of oil, water and dust before coating.

5.3  Excess coating shall be removed before cure so that fins are not bridged.

# 6. Dry film thickness

6.1  Dry film thickness: [x–y] μm, within the range given in the coating TDS.

6.2  Measurement: on witness panels of the same metal coated and cured with each batch, by eddy-current gauge (ISO 2360) or by film weight, and on flat coil areas. The method, locations and number of readings shall be recorded.

# 7. Cure

7.1  The coating shall be cured as stated in its TDS. Part temperature and time (oven cure), or ambient conditions and time (ambient cure), shall be recorded for each batch.

7.2  Coils shall not be packed before the recorded cure is complete.

# 8. Performance evidence

| Property | Requirement | Evidence |
| --- | --- | --- |
| Salt spray | [standard, e.g. ASTM B117 or ISO 9227 NSS]; minimum [ ] h; failure criterion [ ] | Laboratory report stating substrate and film thickness |
| Heat transfer | Capacity loss not more than [ ] % at the specified film thickness | Before-and-after test report with method and coil geometry |
| Air-side pressure drop | Increase not more than [ ] % at [ ] m/s face velocity | Before-and-after test report |
| Adhesion | [ISO 2409 grade 0 or 1 / ASTM D3359 5B or 4B] | Cross-cut test on batch panels |

Salt spray results are comparable only when the standard, substrate, film thickness and failure criterion are the same. Do not rank results measured to different standards.

# 9. Quality control

- Coverage inspection of every coil, including fin roots, tube bends and brazed joints.

- Fin bridging check on the air inlet and outlet faces of every coil.

- Dry film thickness measured for every batch against clause 6.

- Cure record for every batch against clause 7.

- Cross-cut adhesion on panels cured with the batch.

- Photo record of incoming condition, coating and packing.

# 10. Submittals and records

10.1  Before production: TDS, SDS, test reports for clause 8, application method statement and, for new systems, a first-article report for approval.

10.2  With the goods: batch QC report including coating batch and mix, cure record, film thickness record, inspection results and photos, and the warranty certificate.

# 11. Packing and transport

11.1  Coils shall be packed only after full cure, with fin faces protected against impact and the goods protected against moisture and salt air in transit.

# 12. Warranty

12.1  The applicator shall warrant coverage, adhesion and cure of the applied coating for [period] at the site category in clause 2, subject to the stated cleaning and handling conditions.

12.2  Where the coating is specified by the purchaser, the applicator is responsible for application quality and the coating manufacturer for the performance of the coating.

# 13. Handling and maintenance

13.1  Coated coils shall be cleaned with low-pressure water and neutral cleaners only. High-pressure washing, strong acid or alkaline cleaners and abrasive tools are not permitted.

13.2  Damage found on arrival or after installation shall be recorded with photos and touched up with an ambient-cure system before the unit enters service.